## ITP
Inspection & Test Plan — LC-1000 Liquid Cooling Skid
Operation-level inspection and test requirements with owner quality points and required records.
DOCUMENT ID | MQA-ITP-001
REVISION | A
DATE | September 2026
PREPARED BY | Mohammad Al-Araidah
STATUS | Issued for independent engineering study
CLASSIFICATION | Synthetic data — not for production use
INDEPENDENT ENGINEERING STUDY — the supplier, equipment, specifications and all results in this workbook are synthetic. Not design guidance, not a compliance assessment against any standard, and not for use on a production programme.
Equipment: Northstar Thermal Systems LC-1000 — Liquid-to-liquid coolant distribution skid, nominal 1 MW
STEP | MANUFACTURING OPERATION | CHARACTERISTIC | REFERENCE REQUIREMENT | INSPECTION / TEST METHOD | ACCEPTANCE CRITERIA | SAMPLING | SUPPLIER RESPONSIBILITY | OWNER QUALITY POINT | RECORDS REQUIRED | STATUS
010 | Material receipt — piping, fittings, plate | Material specification and grade | Drawing / BOM, material specification register | Certificate review against BOM plus receiving inspection for identification and damage | Material grade and heat identification match the certificate and the BOM; no transit damage | 100% certificate review; 100% identification check | Perform and record | R | Material certificates, receiving inspection record
020 | Material receipt — pumps, heat exchanger, instruments | Configuration and nameplate conformity | Purchase order, approved component data sheets | Nameplate and data-sheet verification against the purchase order, including impeller trim on each pump | Nameplate data, model and impeller trim match the purchase order and the approved data sheet | 100% of major components | Perform and record | W | Component verification record with nameplate data, pump impeller trim record
030 | Instrument calibration verification | Calibration status of test and process instruments | Calibration procedure; instrument list | Calibration certificate review; range and resolution check against the acceptance values to be measured | All instruments within calibration; range and resolution adequate for the acceptance criteria | 100% of instruments used for acceptance measurements | Perform and record | R | Calibration certificates, instrument list with range and due date
040 | Weld fit-up | Joint preparation, alignment, root gap | Approved WPS; fabrication drawings | Visual inspection against the WPS and drawing | Fit-up within the WPS range; joint configuration per drawing | Per supplier procedure | Perform and record | S | Fit-up inspection record by joint identifier
050 | Welding | Procedure and personnel qualification; weld quality | Approved WPS supported by PQR; welder qualification records | Record verification plus visual examination; NDE where specified by joint class | Each weld produced under an approved WPS by a currently qualified welder; visual and NDE results meet the applicable acceptance criteria | 100% visual; NDE per the joint class on the drawing | Perform and record | W | Weld record by joint identifier, welder and WPS; NDE reports
060 | Piping assembly and supports | Configuration, routing, support and flexibility provisions | Piping drawings and support details | Dimensional and visual inspection against the drawings | As-built routing and supports per drawing; no unsupported spans beyond the detail | 100% visual; dimensional on defined features | Perform and record | S | Assembly inspection record, as-built markup
070 | Hydrostatic pressure test | Pressure integrity and leakage | Test procedure; design pressure from the specification | Hydrostatic test at 1.5 × design pressure with a defined hold period and calibrated gauges | No visible leakage and no unexplained pressure decay over the hold period | 100% of pressure-retaining circuits | Perform and record | H | Pressure test record with gauge identification, pressure trace and hold time
080 | Cleanliness and flushing | Internal cleanliness of both circuits | Flushing procedure; filtration specification | Flush to the defined endpoint; filter inspection; capping of open connections after flush | Flush endpoint achieved; no residual debris on filter inspection; all connections capped | 100% of both circuits | Perform and record | W | Flushing record, filter inspection record, capping confirmation
090 | Pump installation and alignment | Alignment and rotation | Pump manufacturer installation requirements | Alignment measurement; uncoupled rotation check | Alignment within the pump manufacturer tolerance; correct direction of rotation | 100% of pumps | Perform and record | W | Alignment record per pump, rotation check record
100 | Electrical assembly and wiring | Drawing conformity, terminations, protection and labelling | Electrical schematics and panel layout | Point-to-point verification; insulation and continuity checks; visual workmanship inspection | Wiring per schematic; insulation and continuity results within limits; all terminations labelled | 100% point-to-point on control circuits | Perform and record | S | Wiring verification record, electrical test results
110 | Configuration freeze | As-built configuration and software revision | Configuration list; released revision list | Record the as-built configuration including PLC application and instrument firmware revisions | As-built configuration recorded and matches the released revisions; any difference covered by an approved deviation | 100% | Perform and record | R | As-built configuration record with software and firmware revisions
120 | Instrument loop check | Sensor scaling and indication | Instrument index; control narrative | Loop check with a known input; verify indication at the HMI and over the BMS interface | Indicated value matches the applied input within the stated instrument accuracy across the range | 100% of loops used for control, alarm or acceptance | Perform and record | W | Loop check record per instrument including scaling and applied values
130 | Controls functional test — alarms and interlocks | Alarm, interlock and emergency-stop function | Functional specification; control narrative | Induce each condition and verify the annunciation, the interlock action and the fail-safe state | Every alarm and interlock operates as specified and returns to a defined safe state | 100% of alarms and interlocks | Perform and record | W | Functional test record listing each condition, action and result
140 | BMS communication test | Interface points and behaviour on loss of communication | Interface point list; control narrative | Verify each point end to end; simulate loss of communication | All points readable and correctly scaled; defined behaviour on communication loss | 100% of interface points | Perform and record | W | Interface point verification record
150 | Performance test — flow and differential pressure | Secondary circuit hydraulic performance | Specification: design flow and minimum differential pressure | Instrumented test at design flow with the test loop set to the design operating point | Differential pressure at or above the specified minimum at design flow, sustained over the defined period | 100% of skids | Perform and record | H | Performance test record with flow, differential pressure, pump speed and instrument identification
160 | Performance test — thermal and control response | Heat transfer and control stability | Specification: capacity, supply temperature setpoint | Instrumented test at design conditions; step change in load to observe control response | Supply temperature held within the specified band at design conditions; control response stable with no sustained oscillation | 100% of skids | Perform and record | W | Thermal performance record, control response trace
170 | Pump redundancy and changeover test | N+1 changeover behaviour | Control narrative; redundancy requirement | Fail the duty pump and verify automatic changeover while flow is maintained | Standby pump starts and design flow is re-established within the specified time, with correct annunciation | 100% of skids, both directions | Perform and record | W | Changeover test record with time to re-establish flow
180 | Leak detection test | Detection, annunciation and fail-safe action | Control narrative; leak detection specification | Simulate a leak at each detection zone and verify the response | Leak detected and annunciated at every zone; specified fail-safe action executed | 100% of detection zones | Perform and record | W | Leak detection test record by zone
190 | Final inspection and preservation | Workmanship, labelling, valve identification, preservation for shipment | Final inspection checklist; preservation and packing specification | Independent final inspection against the checklist; preservation and packing verification | Checklist complete with no open items; preservation and protection per specification | 100% | Perform and record | W | Final inspection record, preservation and packing record, photographic record
200 | Documentation turnover | Completeness of the turnover package | Turnover documentation index | Document review against the index, item by item | Every indexed document present, legible, at the correct revision and traceable to the skid serial number | 100% of the index | Compile and submit | H | Turnover package with index and completion sign-off

## Quality points
Inspection & Test Plan — LC-1000 Liquid Cooling Skid
Operation-level inspection and test requirements with owner quality points and required records.
DOCUMENT ID | MQA-ITP-001
REVISION | A
DATE | September 2026
PREPARED BY | Mohammad Al-Araidah
STATUS | Issued for independent engineering study
CLASSIFICATION | Synthetic data — not for production use
INDEPENDENT ENGINEERING STUDY — the supplier, equipment, specifications and all results in this workbook are synthetic. Not design guidance, not a compliance assessment against any standard, and not for use on a production programme.
CODE | POINT | DEFINITION
R | Review | Owner reviews the record after the fact. Work proceeds without waiting; a finding is handled as a nonconformance.
S | Surveillance | Owner may observe at its discretion without notification. Work is not gated on the owner being present.
W | Witness | Owner is notified and may attend. If the owner does not attend by the agreed time, work may proceed and the record is reviewed instead.
H | Hold | Work may not proceed past this point without owner release. Chosen only where the evidence becomes unavailable or unaffordable to obtain afterwards.

## Equipment
Inspection & Test Plan — LC-1000 Liquid Cooling Skid
Operation-level inspection and test requirements with owner quality points and required records.
DOCUMENT ID | MQA-ITP-001
REVISION | A
DATE | September 2026
PREPARED BY | Mohammad Al-Araidah
STATUS | Issued for independent engineering study
CLASSIFICATION | Synthetic data — not for production use
INDEPENDENT ENGINEERING STUDY — the supplier, equipment, specifications and all results in this workbook are synthetic. Not design guidance, not a compliance assessment against any standard, and not for use on a production programme.
PARAMETER | VALUE | BASIS | SOURCE OR DERIVATION
Nominal thermal capacity | 1 MW | Study assumption | Chosen as a representative single-skid capacity so the quality problem is concrete. Not derived from any product.
Architecture | Liquid-to-liquid, separated facility (primary) and technology (secondary) circuits | Design context | A CDU transfers heat between dedicated liquid loops and provides pressure, flow, temperature, dew-point control, cleanliness and leak detection (OCP Cooling Environments).
Secondary (technology) supply temperature | 32 °C maximum | Study assumption | Selected to sit at the ASHRAE W32 facility water class boundary. The class exists; selecting it for this skid is a study assumption.
Primary (facility) supply temperature | 27 °C maximum | Study assumption | Selected at the ASHRAE W27 class boundary to give a workable approach temperature across the heat exchanger.
Secondary circuit temperature rise | 10 K | Study assumption | Chosen to set the design flow. A different ΔT would change flow and therefore every hydraulic acceptance value below.
Secondary design flow | 1,440 L/min (24 L/s) | Acceptance requirement | Derived: 1,000 kW ÷ (4.18 kJ/kg·K × 10 K) ≈ 23.9 kg/s ≈ 24 L/s. Rounded to 1,440 L/min, which returns a 10.0 K rise at capacity.
Secondary differential pressure at design flow | 250 kPa minimum | Acceptance requirement | The head the skid must deliver to the technology loop at design flow. Assumed for this study; on a real project it comes from the downstream loop resistance.
Circuit design pressure | 1,000 kPa (10 bar) | Study assumption | Chosen to make the pressure-test acceptance value derivable rather than asserted.
Hydrostatic test pressure | 1,500 kPa | Acceptance requirement | Derived as 1.5 × design pressure, the minimum hydrostatic leak-test pressure in ASME B31.3, subject to not exceeding the rating of any non-isolated component.
Circulation pumps | Two, N+1, each rated for 100% design flow, VFD driven | Study assumption | Redundancy configuration chosen so that pump changeover becomes a testable acceptance criterion.
Pump control mode | Constant differential-pressure setpoint on the secondary circuit | Study assumption | Determines what the controls and performance tests have to demonstrate.
Heat exchanger | Gasketed plate-and-frame, 3 K approach | Study assumption | Approach temperature chosen to be consistent with the 27 °C primary and 32 °C secondary assumptions above.
Secondary-side filtration | 50 µm | Design context | OCP reports typical technology-cooling-system loop filtration of 25–50 µm, set by the most particle-sensitive component in the loop.
Primary-side filtration | 250 µm | Design context | OCP reports typical facility-side filtration of 150–250 µm depending on design and customer requirements.
Wetted materials | Stainless steel piping, compatible elastomers, validated against the specified coolant | Design context | Material compatibility between wetted materials and the cooling liquid must be validated for all liquid-cooling components (OCP).
Instrumentation | Pressure, temperature and flow on both circuits; differential-pressure transmitter across secondary supply and return | Study assumption | Instrument set chosen so every performance acceptance criterion can actually be measured on the skid.
Controls | PLC with local HMI; BMS interface over Modbus TCP; alarm and interlock set; fail-safe state defined | Study assumption | Defines the scope of the controls section of the FAT.
Leak detection | Skid-level leak detection with alarm to the BMS and defined fail-safe action | Design context | Leak detection is named as a CDU function in OCP Cooling Environments documentation.
Expansion & make-up | Bladder expansion tank on the secondary circuit with low-level alarm | Study assumption | Included so the pressure-control scope of the FAT is complete.